City of Maple Ridge

Whonnock Well

Water Quality Report 2019

WHONNOCK WELL

WATER QUALITY REPORT 2019

Table of Contents

1	EXECUTIVE SUMMARY	3

2	INTRODUCTION	4

3	BACKGROUND	5

3.1	OUTLINE	5

3.2	FACILITY MAINTENANCE	5

3.3	WHONNOCK WELL WATER SYSTEM ROUTINE SAMPLING AND EMERGENCY RESPONSE PROTOCOL	5

3.4	CORRECTIVE MEASURES AND MAINTENANCE	6

3.5	WATER QUALITY SAMPLING AND MONITORING	7

4	EMERGENCY RESPONSE	9

4.1	NOTIFICATION REQUIREMENTS	9

4.2	E. COLI POSITIVE SAMPLES – RESPONSE PROCEDURE	9

5	DRINKING WATER QUALITY MONITORING RESULTS	9

6	CONCLUSION	10

APPENDIX A – HPC VS TEMPERATURE GRAPH	11

APPENDIX B – HPC VS TEMPERATURE & TURBIDITY GRAPH	12

APPENDIX C – WEEKLY SAMPLE	13

APPENDIX D – ANNUAL MATERIAL ANALYSIS	17

City of Maple Ridge

December 2019

# EXECUTIVE SUMMARY

The City of Maple Ridge provides well water at the Whonnock well site, under permit by the Fraser Health Authority (FHA). It contains a storage tank, two filters, two backflow preventers and an ultraviolet disinfection unit along with a push button dispenser for the user. Whonnock well is a 36m deep well which provides water for citizens living in the 272 Street area. It was drilled in 1981, 2018 the well casing was cleaned and video inspected proving to be in good condition, a new pump was installed and well capacity tested. The well is primarily used by the residents in the Whonnock area, the operating and maintenance costs are funded by water utility tax that Whonnock residents do not pay into. The City is assessing all the possible options available to keep this well operating and extend the wells lifespan with future upgrades.

Outside Tap and Push Button

# INTRODUCTION

This document is the City of Maple Ridge’s report on the Whonnock well, located at 10919 272 Street. This report is prepared for public information.

Contents of the report include an outline of the regulatory framework and water quality monitoring data and results for the year 2019.

Ultraviolet Disinfection Unit

# BACKGROUND

## OUTLINE

Whonnock well is a low-volume water well located at 10919 272 Street. The existing connection is 32mm in diameter with a male pipe thread. An ultraviolet disinfection unit preceded by two filters was added in August of 2001 as part of our water quality improvements work. The maximum discharge is 40 liters per minute (9 gallons/min).

## FACILITY MAINTENANCE

Whonnock well is maintained by the City of Maple Ridge > Public Works & Development Services > Operations Centre. Their duties involve sampling and routine maintenance of the equipment within the Whonnock well structure. The operation and maintenance costs are not recovered from Whonnock residents.

## WHONNOCK WELL WATER SYSTEM ROUTINE SAMPLING AND EMERGENCY RESPONSE PROTOCOL

These procedures were revised in February 2008 reviewed in 2019 and approved by the FHA.

Routine Water Sampling

Water samples are taken every Tuesday morning by the Waterworks section of the Operations Centre. A courier delivers these samples the same day to the Metro Vancouver Water Department laboratory. The laboratory reports the analysis results via email by Monday of the following week and that email is sent to the following municipal personnel as well as the FHA:

- James Storey 	– Director of Engineering Operations 	– 604-463-9581

- Davin Wilson	– Superintendent of Waterworks	– 604-463-9581

- Aaron Schramm	– Supervisor 3 of Waterworks	– 604-463-9581

- Mike Gjaltema	– Electro/Mechanical Manager 	– 604-463-9581

- Mitch Stripp 	– Supervisor of Electrical Mechanical 	– 604-463-9581

- Bruce Gailling 	– Electronics Technician 	– 604-463-9581

- Rob Dyer 	– Trades Inspector 	– 604-476-3076

Emergency Response Protocol

As per the Whonnock Well Emergency Response Protocol, in the event of a concern discovered upon analysis the Metro Vancouver Water Department laboratory will email those listed above. Personnel in the Electro-Mechanical section will be the first responders, or alternatively, any of the above-noted personnel. The well will be shut down immediately, the FHA will be notified and a notice will be posted advising the users about alternate sources of water.

All after-hours, weekend or statutory holiday calls will be made to the Operations Centre standby personnel via Surrey Dispatch.

The expected triggers for this Emergency Response Protocol are listed below:

- Unsatisfactory bacterial results.

- A resident’s report of bad smell, colour or taste.

- Environmental hazards or spills around the well.

- Motor vehicle accident causing damages to the building or installations.

- Vandalism to the building or installations.

- Pump failure.

- Breach of security.

## CORRECTIVE MEASURES AND MAINTENANCE

The facility is inspected weekly and the filters are changed when they have been in use for three months or if the discharge flow drops to 30 liters a minute.

The ultraviolet lamp used in the disinfection unit is replaced annually.

When dealing with a possible problem with the water quality of the Whonnock well, the following steps are followed by staff:

- Turn off the system and post outside one of the notifications “Well shut down due to a bad sample” or, “due to maintenance.”

- Inspect the integrity of the system (ensuring that nothing was tampered with or changed).

- Check the operation of the ultraviolet disinfection, filtration, hoses or any other mechanical components.

- Once the defective condition has been located and resolved or repaired, the Operations Centre Waterworks section will collect three separate samples on the following Monday, Tuesday and Wednesday to be sent to the Metro Vancouver Water Department laboratory for analysis. If all three analyses return within acceptable limits, FHA will be notified and, with their agreement, the system can be reactivated and the warning signs removed.

- If any of the lab results continue to read as unacceptable and no remedial measures are effective, the FHA must be informed.

- When an isolated report outside of routine water testing occurs (i.e. residents report bad smell, colour, taste or high turbidity), the above protocol will be immediately activated. The Operations Centre Waterworks section will collect a sample to be sent to the Metro Vancouver Water Department laboratory for analysis.

- No action required in case of power failure: there is no water dispensed when the power is out.

## WATER QUALITY SAMPLING AND MONITORING

Samples are taken weekly by the City of Maple Ridge’s Operations Department staff and sent to the Metro Vancouver Water Department laboratory for analysis. The Metro Vancouver Water Department laboratory sends the results to the City of Maple Ridge and the FHA by email (these results are fully tabulated for 2019 in Appendix C).

In addition, an annual water chemical analysis is performed. For this annual analysis, the City of Maple Ridge uses a laboratory that can provide the necessary accuracy in determining the arsenic level. This was necessary after the changes in 2006 in Health Canada’s arsenic guidelines and to demonstrate compliance. The test results are attached in Appendix D.

It is important to note that this water quality monitoring program provides a representative picture of drinking water quality in the well system to the well tap. However, it does not provide a definite picture of drinking water quality once the user has obtained the water from the well.

Bacteriological Monitoring

Weekly samples are analyzed for E. Coli, total coliform and heterotrophic plate count (HPC) as shown in Appendix C.

Table 1

BC Drinking Water Protection Regulation Microbiological Standards

(Extracted from Appendix A)

| Parameter | Occurrence | Standard |
| --- | --- | --- |
| E. Coli | 1 sample | Less than 1 fecal coliform per 100mL |
| Total Coliform | a) 1 sample in a 30 day period | 0 total coliform per 100mL |
|  | b) more than 1 sample in a 30 day period. | At least 90% of samples have 0 total coliform per 100mL and no sample has more than 10 total coliform per 100mL |

Chemical and Physical Monitoring

A table of the City of Maple Ridge’s chemical and physical monitoring schedule is noted in Table 2. The report from Bodycote Testing Group Laboratory can be viewed in Appendix D.

Table 2

Chemical/Physical Monitoring in Municipal Distribution Systems

| Parameter | Frequency |
| --- | --- |
| Temperature | Weekly |
| Copper | Annually |
| Iron | Annually |
| Lead | Annually |
| Odour | On Complaint Basis |
| PH | Annually |
| Taste | On Complaint Basis |
| Trihalomethanes | Annually |
| Turbidity | Weekly, collected with bacteriological samples |
| Zinc | Annually |
| E. Coli | Weekly |
| Aluminum | Annually |
| Arsenic | Annually |
| Barium | Annually |
| Boron | Annually |
| Cadmium | Annually |
| Calcium | Annually |
| Chromium | Annually |
| Cobalt | Annually |
| Magnesium | Annually |
| Manganese | Annually |
| Sodium | Annually |

# EMERGENCY RESPONSE

## NOTIFICATION REQUIREMENTS

The various agencies would be notified in the situations shown in Table 3.

Table 3

Notification for Unusual Situations Affecting Water Potability

| Situation | Notifying Agency | Agency Notified | Time Frame For Notification |
| --- | --- | --- | --- |
| E. Coli Positive Sample | Metro Van Laboratory | FHA City of Maple Ridge | Immediate |
| Chemical Contamination | City of Maple Ridge | FHA | Immediate |
| Turbidity >5 NTU | Metro Van Laboratory | FHA City of Maple Ridge | Immediate |
| Disinfection Failure - Source Water (Primary Disinfection) | City of Maple Ridge | FHA | Immediate |

## E. COLI POSITIVE SAMPLES – RESPONSE PROCEDURE

If a sample analyzed by the Metro Vancouver Water Department laboratory tests positive for E. Coli, the well will be shut down immediately and will remain out of service until the problem is rectified. Action: shut the system down, flush and disinfect with chlorine. Re-sample twice over two days and re-activate the well if no E-coli is present.

# DRINKING WATER QUALITY MONITORING RESULTS

No samples tested positive for total coliform bacteria in 2019, the same as in previous years. There were no samples testing positive for E. Coli and no samples containing more than 10 total coliform per 100ml, therefore the microbiological standards were met for 2017.

Heterotrophic plate counts (HPC) are also recorded in weekly samples. Although there is no standard for maximum CFU per mls, the US standard is 500 CFU/mls. HPC is a procedure for estimating the number of live heterotrophic bacteria in water and measuring changes during water treatment and distribution. A passage about what HPC counts keep track of is shown below (Heterotrophic Plate Counts and Drinking-water Safety, WHO, 2003):

“Heterotrophs are broadly defined as microorganisms that require organic carbon for growth. They include bacteria, yeasts and moulds. A variety of simple culture-based tests that are intended to recover a wide range of microorganisms from water are collectively referred to as “heterotrophic plate count” or “HPC test” procedures. Accordingly, the terms “heterotroph” and “HPC” are not synonymous. There is no universal “HPC measurement.” Although standardized methods have been formalized, HPC test methods involve a wide variety of test conditions that lead to a wide range of quantitative and qualitative results.

Temperatures employed range from around 20°C to 40°C, incubation times from a few hours to seven days or a few weeks and nutrient conditions from low to high. The test itself does not specify the organisms that are detected. Only a small proportion of the metabolically active microorganisms present in a water sample may grow and be detected under any given set of HPC test conditions and the population recovered will differ significantly according to the method used. The actual organisms recovered in HPC testing can also vary widely between locations, between seasons and between consecutive samples at a single location. Microorganisms recovered through HPC tests generally include those that are part of the natural (typically non-hazardous) microbiota of water; in some instances, they may also include organisms derived from diverse pollutant sources.”

In 2019, only 1 out of 50 tests had readings above 500 HPC [CFU/mls]. The average count was 132.9 HPC [CFU/mls] for that site.

A sign has been permanently posted that advises users to run the water for 15 seconds before filling up, in order to remove stagnant water within the pipe.

# CONCLUSION

This report provides an outline of the water quality of the Whonnock well, as well as the initiatives and program being performed by the City of Maple Ridge.

# APPENDIX A – HPC VS TEMPERATURE GRAPH

# APPENDIX B – HPC VS TEMPERATURE & TURBIDITY GRAPH

# APPENDIX C – WEEKLY SAMPLE

| Sampling Point | Sample Type | Sample Reported Name | Sampled Date | Fcoli MPN/100 mLs | (Max 500) HPC CFU/mLs | TEMP ◦C | Tcoli MPN/100 mLs | Turbility NTU |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MPR-WP1 | GRAB | Whonnock Well Tank | 1/3/2019 11:48 | <1 | 260 | 10 | <1 | 0.5 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 1/8/2019 12:05 | <1 | 340 | 11 | <1 | 0.53 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 1/15/2019 10:50 | <1 | 76 | 10 | <1 | 0.33 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 1/22/2019 8:49 | <1 | 96 | 11 | <1 | 0.2 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 1/29/2019 11:05 | <1 | 96 | 9 | <1 | 0.47 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 2/5/2019 11:20 | <1 | 170 | 9 | <1 | 0.23 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 2/12/2019 10:35 | <1 | LA | 6 | <1 | 0.48 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 2/19/2019 10:25 | <1 | 86 | 9 | <1 | 1.4 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 2/26/2019 10:20 | <1 | 230 | 9 | <1 | 0.97 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 3/5/2019 10:15 | <1 | 270 | 8 | <1 | 1.8 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 3/12/2019 11:20 | <1 | 110 | 8 | <1 | 0.16 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 3/19/2019 10:39 | <1 | 8 | 8 | <1 | 2.3 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 3/26/2019 11:05 | <1 | 10 | 11 | <1 | 0.85 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 4/2/2019 10:15 | <1 | 28 | 11 | <1 | 0.67 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 4/9/2019 10:15 | <1 | 80 | 11 | <1 | 1.2 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 4/16/2019 10:25 | <1 | 60 | 11 | <1 | 0.55 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 4/23/2019 10:32 | <1 | 84 | 12 | <1 | 0.44 |
| Sampling Point | Sample Type | Sample Reported Name | 4/30/2019 11:02 | <1 | 62 | 11 | <1 | 0.83 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 5/7/2019 10:40 | <1 | 50 | 11 | <1 | 0.73 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 5/14/2019 10:15 | <1 | 120 | 12 | <1 | 0.79 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 5/21/2019 10:31 | <1 | 74 | 12 | <1 | 0.44 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 5/28/2019 11:15 | <1 | 12 | 13 | <1 | 0.54 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 6/4/2019 10:40 | <1 | 24 | 13 | <1 | 0.52 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 6/11/2019 11:38 | <1 | 38 | 12 | <1 | 0.41 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 6/18/2019 10:35 | <1 | 64 | 12 | <1 | 1.1 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 6/25/2019 10:40 | <1 | 113 | 12 | <1 | 1.7 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 7/2/2019 10:35 | <1 | 80 | 13 | <1 | 0.81 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 7/9/2019 10:30 | <1 | 120 | 13 | 2 | 0.16 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 7/16/2019 10:30 | <1 | 160 | 12 | <1 | 0.66 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 7/23/2019 11:19 | <1 | 110 | 12 | <1 | 0.53 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 7/30/2019 10:50 | <1 | 86 | 12 | <1 | 0.63 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 8/6/2019 10:30 | <1 | 120 | 13 | <1 | 1 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 8/13/2019 10:15 | <1 | 280 | 13 | <1 | 0.89 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 8/20/2019 12:27 | <1 | 920 | 12 | <1 | 1.2 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 8/27/2019 10:36 | <1 | 2 | 11 | <1 | 0.71 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 9/3/2019 10:48 | <1 | 150 | 11 | <1 | 0.6 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 9/10/2019 10:30 | <1 | 212 | 12 | <1 | 1.6 |
| Sampling Point | Sample Type | Sample Reported Name | 9/17/2019 10:40 | <1 | 230 | 14 | <1 | 1.9 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 9/24/2019 11:12 | <1 | 100 | 12 | <1 | 1.5 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 10/1/2019 10:36 | <1 | 36 | 12 | <1 | 0.45 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 10/8/2019 11:24 | <1 | 52 | 11 | <1 | 0.36 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 10/15/2019 10:30 | <1 | 60 | 11 | <1 | 0.4 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 10/22/2019 13:30 | <1 | 440 | 15 | <1 | 1.5 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 10/29/2019 10:36 | <1 | 250 | 11 | <1 | 0.38 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 11/5/2019 11:20 | <1 | 470 | 9 | <1 | 0.41 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 11/12/2019 10:45 | <1 | 22 | 11 | <1 | 0.28 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 11/19/2019 11:21 | <1 | 12 | 12 | <1 | 0.28 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 11/26/2019 11:00 | <1 | 18 | 11 | <1 | 0.33 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 12/3/2019 11:18 | <1 | 4 | 9 | <1 | 1.7 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 12/10/2019 10:45 | <1 | 140 | 7 | <1 | 0.66 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 12/17/2019 11:07 | <1 | 14 | 9 | <1 | 0.34 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 12/23/2019 11:00 | <1 | N/A | 6 | <1 | 0.2 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 12/30/2019 10:40 | <1 | N/A | 6 | <1 | 0.8 |
| MPR-WP1 | GRAB | Whonnock Well Tank | 1/3/2019 11:48 | <1 | 260 | 10 | <1 | 0.5 |

METRO VANCOUVER WATER DEPARTMENT LABORATORY RESULTS

# APPENDIX D – ANNUAL MATERIAL ANALYSIS

Metro Vancouver for samples being processed by Metro Vancouver Water Department laboratory.

BCDWPR requires the laboratory to notify public health.

See Section 4.2